CYLINDER RETEST STATIONS

AIGA xxx/08

AIGA xxx/08

CYLINDER

RETEST STATIONS

Replace with AIGA Disclaimer

Acknowledgement

This document is adopted from the European Industrial Gases Association IGC Document 79/07 E

‘Cylinder retest stations’.  Acknowledgement and thanks are hereby given to EIGA for permission granted for the use of their document.

Table of Contents

1	Introduction	1

2	Scope and Purpose	1

3	Background to Periodic Inspection and Testing	1

4	Test Stations	1

4.1	Test Stations Organisation	2

4.2	Test Station Facilities and Procedures - General	2

4.2.1	General	2

4.2.2	Devalving	2

4.2.3	Inspection and Cleaning	2

4.2.4	Weighing	3

4.2.5	Test Equipment	3

4.2.6	Drying	3

4.2.7	Painting	3

4.2.8	Repairs	3

4.3	Acetylene Cylinders Periodic Inspection - Specific Requirements	3

4.4	Procedures	4

4.5	Records	4

4.6	Valves	4

4.8	Bibliography	5

# Introduction

The periodic inspection and testing of a gas cylinder is an essential requirement for its continued use. There are few items of industrial equipment that last for so many years. The safety record of these cylinders is excellent and reflects the integrity of the design, manufacturing and subsequent maintenance processes.

# Scope and Purpose

This document gives guidance on the key aspects of the periodic inspection and retesting of gas cylinders and gives a structure for the re-testing activity. It is intended specifically for those who are:

- Specifying the Periodic Inspection and Testing of Gas Cylinders

- Selecting Inspection and Testing Facilities

- Carrying out the Periodic Inspection and Testing Process

The following cylinder types are covered in the document:

- Seamless Steel

- Welded Steel

- Seamless Aluminium Alloy

- Welded Aluminium Alloy

- Hoop Wrapped

- Fully Wrapped

- Dissolved Acetylene

Additional requirements, which may apply for specific applications such as medical, electronics, are not covered in this document.

.

# Background to Periodic Inspection and Testing

The periodic inspection and testing of gas cylinders has been a requirement for many years across a wide range of countries. This inspection requirement has frequently been part of the legal requirement of operating a gas cylinder, and failure to follow a prescribed test programme has been treated as a serious offence.

The requirement to test and inspect gas cylinders has evolved as National Requirements, with the test periods and the test frequencies being set by the National bodies. A summary of the cylinder retest regulations in some of the countries in Asia is shown in appendix 1.

.[AIGA comment: This paragraph was proposed for deletion. As there are a number of references to PED and European EN standards throughout the document, it may be better to keep this , but perhaps put it within brackets ]

# Test Stations

Test stations shall be compliant with the requirements of the National Competent Authority. For cylinders retested under the requirements of the Transportable Pressure Equipment Directive, the appointed Inspection Bodies, either Notified or Approved, shall comply with the criteria as stated in Annexes 1 and 2 of Council Directive 1999/36/EC [n].

## Test Stations Organisation

Personnel involved in the retesting of gas cylinders shall be suitably qualified for the purpose and the quality of the work shall be under no commercial pressure. Specific country regulatory requirements should be met with regard to the competency and number of years of experience required for the personnel operating the testing stations.

## Test Station Facilities and Procedures - General

### General

a)	There shall be adequate lighting, ventilation and workspace for the inspection and testing. Additionally the work areas shall be clean and free of debris.

b)  The test stations must have the approved procedures as per the local reguirements and also national/international standards.

c)  Test stations with hydrostatic test facility should have two separate test heads. One test head should be marked green, for example, for dedicated ‘clean’ service cylinders used for gases such as synthetic air, oxygen, nitrous oxide, etc.  All other cylinders should be tested by using another test head, painted red, for example, dedicated for ‘non-clean’ service cylinders.

d) 	Test stations shall be equipped to vent gases in a safe manner which shall direct gases released, away from the work place, to an area where no risk is presented, e.g. to a high level.

Gas cylinders containing controlled substances, e.g. toxic, corrosive, ozone depleting and flammable gases, etc shall only be handled at locations with specialist facilities to dispose of these products that meet applicable environmental and safety considerations.

### Devalving

Warning: Devalving of cylinders is a potentially hazardous activity if not carried out correctly.  Before any cylinder is devalved a positive check shall be carried out to ensure there is no pressure in the cylinder, for guidance see EIGA Safety Information 18/04 and ISO CD 25760 [q]

a) There shall be procedures and mechanisms in place to protect the operative against a cylinder under pressure being accidentally devalved. Specific guidance is given in the appropriate EN standards, e.g. EN 1968 [e] and CD ISO 25760 [q]. Valves shall not be repaired or removed while the cylinder is under pressure.  There are no exceptions to this rule.

- It is critical that working procedures describe the process to check if a valve is functioning correctly or if it is blocked. Additionally some valves are designed to retain a small positive pressure in the cylinder, and care is needed to ensure that cylinders are completely vented when fitted with these valves, see [c, d, e, f, k].

- There shall be equipment to de-valve and re-valve cylinders. This equipment shall not damage the cylinder, e.g. during clamping, particularly of aluminium alloy or composite cylinders, or damage to the valve unnecessarily.

### Inspection and Cleaning

For hazardous gases, such as toxic and flammables, care shall be taken to ensure that cylinders have been adequately purged and/or evacuated to ensure that a hazardous atmosphere is not present prior to internal inspection and cleaning.

a)	Test stations shall have access to both internal and external cleaning facilities. Examples of cleaning methods include shot blasting and high-pressure water jet cleaning. Where heat is applied to the cylinder, care shall be taken to ensure that the temperature limits specified are not exceeded, this specifically applies to aluminium alloy and composite cylinders, see e.g. ISO 10461 [o].

Note: Aluminium alloy cylinders shall not be shot blasted due to their soft nature and the possibility of galvanic corrosion. Other cleaning methods, e.g. sand cleaning or wire brushing shall be carefully evaluated, preferably in conjunction with the cylinder manufacturer. For cleaning composite cylinders see EN 11623 [f].

b)	There shall be equipment to examine and clean cylinder neck threads that does not cause damage to the thread. There shall be thread gauges for checking neck threads as required, and taps for any refurbishment. In all cases there shall have been training of personnel in the use of these gauges.

- There shall be equipment for the external and internal inspection of cylinders to ensure that a thorough inspection can be made. It is recommended that lamps be sufficiently protected in case the lamp breaks and ignites any residual gas. An alternative, successfully used by a number of organisations, is optical fibre lamps. The light shall be of a suitable intensity that allows all types of defects to be detected. The test station shall have access to equipment to measure the severity of defects where required.

### Weighing

When weighing is required a suitable weigh scale shall be used, for guidance on weigh scale accuracy, see EN 1919, (p).

### Test Equipment

a) 	Test equipment, e.g. hydraulic testing and/or ultrasonics shall fully comply with the requirements of the appropriate testing standards and/or national regulatory requirements.

b) 	There shall be adequate supply and disposal facilities for the fluid used for testing including adequate water treatment where applicable.

Note: If the fluid is recycled, it shall be adequately filtered to prevent carry over of contaminants, such as rust. These filters shall be periodically cleaned.

A check shall be carried out on the pH value of the recycled water. Where both steel and aluminium alloy cylinders are tested, the risk of galvanic corrosion can be minimised by either using separate circuits or imposing additional requirements to the quality and filtering of the water. For additional requirements for aluminium alloy cylinders, see EIGA doc. 72/06 [m]. In some cases, for example, medical oxygen cylinders, there may be a requirement to use drinking water quality for the hydro testing.

If the test fluid is flammable, e.g. when testing LPG cylinders, suitable precautions shall be taken. Cylinders of different types e.g. high Pressure and low pressure such as LPG should not be tested on the same test line. Adequate precautions shall be taken to ensure that there is no cross contamination.

- The testing equipment shall be adequately shielded to protect personnel in the event of a release of test fluid, particularly in the case of pneumatic testing.

### Drying

There shall be adequate drying equipment to ensure that there shall be no free moisture and that this dryness is maintained until the valve is fitted, see EIGA doc. 62/05 [l]. For aluminium alloy cylinders, reference shall be made to ISO 10461[o] for allowable time and temperature limits.

### Painting

There shall be appropriate equipment to paint cylinders in accordance with environmental and colour code requirements, [b]. For aluminium alloy cylinders, reference shall be made to ISO 10461[o] for allowable time and temperature limits.

### Repairs

Repairs to cylinders when required shall only be carried out in accordance with the relevant standards by trained and qualified personnel only.. Major repairs, which include, for example welding and heat treatment, are normally only accepted on welded steel and welded aluminium alloy cylinders.

## Acetylene Cylinders Periodic Inspection - Specific Requirements

- Acetylene cylinders shall only undergo inspection at facilities specifically designated for the purpose. Acetylene inspection facilities shall be designed such that there is no source of ignition of gas.

- Acetylene cylinders shall be vented in a safe manner prior to valve removal and the cylinder confirmed as being empty by weighing. It shall be checked that the valve is not blocked, see CD 25760 [q].

- Due to the risk of the build up of acetylene gas which can occur if there is a rise in the ambient temperature when a cylinder has been devalved and moved from a cold atmosphere to a warmer one, the inspection process shall be performed such that only the minimum number of cylinders are de-valved at any one point in the inspection process to avoid a build up of acetylene gas and a possible explosion. Cylinders shall be devalved with adequate operator protection, see CD 25760, [q].

- As some cylinders with monolithic masses use asbestos as a binder, no work should be carried out on the mass, which could cause asbestos fibres to be released.

- All tools used in the inspection of acetylene cylinders shall not generate sparks, (spark resistant).

- No portable electronic equipment that is not certified for use in an acetylene environment shall be used, e.g. mobile phones, remote control car keys, laptops etc.

## Procedures

- A system shall be in place to show that all procedures are followed and that no stage of the inspection process is omitted.

- The procedures for the cylinder inspection process shall be part of a Quality System.

- There shall be formal written operating instructions for all machinery and equipment.

- For welded cylinders, there shall be equipment to invert the cylinder to enable the external base area to be visually inspected, (including fusible plugs,)

- There shall be procedures to ensure that cylinders are internally inspected and dried before the valve is fitted.

- There shall be procedures for the stamp marking of gas cylinders in accordance with relevant stamp standard marking for gas cylinders, e.g. ISO 13769 [a]

- Current applicable standards shall be available on site for the activity concerned.

- There shall be a planned maintenance and calibration programme for all relevant equipment.

- There shall be a defined system for disposal of cylinders, see EIGA document 05/06, [j] and also  national  standards.

## Records

- Records for the cylinder retest shall be in accordance with the appropriate test standard, e.g. EN 1968, EN 12863, [e,g] , national standards, etc.

- All records including details of calibrations, on-conformities and training of personnel shall be maintained.

## Valves

- There shall be suitable equipment and a system in place to ensure that the appropriate valves are fitted for the service of the gas cylinder and that the valves are installed in accordance with EN ISO 13341 [h] and/or national approved standard where available.. Including the stem thread matches the cylinder internal neck thread. Specifically, care shall be taken to ensure that the maximum permitted torque value is not exceeded

- Where valves are reused, they shall be periodically inspected., [ AIGA comment: I suggest leaving this in as having a reference is better than not having anything]

4.7	Qualification and Training of Personnel

  - There shall be a training scheme in place to ensure that all personnel are adequately trained for the tasks to be carried out.

  - There shall be periodic competency checks of all personnel.

## 4.8	Bibliography

a)	ISO 13769: Gas Cylinders -: Stamp marking

b)	EN 1089-3: Transportable Gas Cylinders - Gas cylinder identification Part 3: Colour Coding

c)	EN 1802: Transportable Gas Cylinders- Periodic Inspection and Testing of  seamless aluminium gas cylinders

d)	EN 1803: Transportable Gas Cylinders- Periodic Inspection and Testing of  welded carbon steel gas cylinders (excluding LPG)

e)	EN 1968: Transportable Gas Cylinders- Periodic Inspection and Testing of  seamless steel gas cylinders

f)	EN ISO 11623:  Transportable Gas Cylinders- Periodic Inspection and Testing of composite gas cylinders

g)	EN 12863: Transportable Gas Cylinders-Periodic Inspection and Maintenance of dissolved acetylene cylinders

h)	EN ISO 13341: Transportable Gas Cylinders Fitting of valves to gas cylinders

- EN 45004: General Criteria for the Operation of various types of bodies performing inspection

j)	EIGA Document 5/06: Guidelines for the Disposal of Acetylene Cylinders

k)	EIGA Document 64/05: Guidelines on the use Residual Pressure Valves

l)	EIGA Document 62/05: Methods to avoid and detect internal gas cylinder corrosion

m)	EIGA Document 72/06: Corrosive effect of tap water on aluminium cylinders

n)	Council Directive 1999/36/EC on transportable pressure equipment

o)	ISO 10461 Seamless aluminium alloy gas cylinders: Periodic Inspection and Testing

p) EN 1919 Transportable Gas Cylinders Cylinders for liquefied gases (excluding dissolved acetylene and LPG) Inspection at time of filling

q)	ISO CD 25760 Gas Cylinders Operational Procedures for the safe removal of valves from gas cylinders

r) EN 14189 Inspection and maintenance of cylinder valves at time periodic inspection of gas cylinders

o)  GB Standards in China

p) Gas Cylinder Rule 2004 and Indian Standard IS 8868 in India

q) High Pressure Gas Safety Control Law in Korea

r) Thialand Industrial Standards (TIS) in Thailand

s) High Pressure Vessel Safety Regulations (draft) in Taiwan

Appendix 1: Summary of some cylinder requalification regulations in Asia by country retest intervals and retest methods

[AIGA comment: Should also include Singapore, Malaysia , Indonesia, Philippines]

| Country | China | Taiwan | Korea | India | Thailand |
| --- | --- | --- | --- | --- | --- |
| Regulation | GB | High Pressure Vessel Safety Regulation (DRAFT) | High Pressure Gas Safety Control Law | GCR (Gas Cylinder Rules) 2004 and Indian Standard IS 8868 | TIS |
| Section of Regulation governing cylinder requalification | GB8334-1999 GB12135-1999 GB13004-1999 GB13075-1999 GB13076-1999 GB13077-1999 | SEC 4 RULE 44~49 (Currently there’s no suitable regulation to manage cylinders safety issue) | SEC 39 and annexed sheet 22. | GCR 2004 : 1. Chapter IV Examination and Testing of Cylinders (Rule 35) 2. Chapter V (Rule 39) Examination of Dissolved Acetylene cylinders before filling 3. Schedule IV (Facilities required for cylinder Testing stations) | TIS359 (Thai Industrial Standard No.359) |
| Retest Interval | 3 or 4 yr for LPG; 2, 3 or 5 yr for Seamless Steel; 2 or 3 yr for Welded; 3 yr for Acetylene; 2, 3 or 5 yr for AL Alloy | 2 or 5 yr for hard welded, casting, ultra low-temp vessel, 5 yr for Seamless 1 yr for AL Alloy 3yr for complex | 1, 2, 3, & 5 years, See below table | 5 years for Inerts, Flammables, O2 & Oxidizers; 2 years for Toxics & Acetylene | 5 years |
| Hydraulic pressure test permitted | Yes | Not defined yet | Yes | Yes | Yes |
| Ultrasonic Examination permitted | No | Not defined yet | No | No | Yes (In approving process) |
| Acoustic Emission permitted | No | Not defined yet | Yes with Visual inspection | No | No |
| External Visual inspection in lieu of Hydrotest permitted (Besides Acetylene) | No | Not defined yet | No | No | Yes, for certain approved gases |